|  | #### Job Safety Analysis |
| --- | --- |

| Control No: |  | Status: |  | Original Date: |  |
| --- | --- | --- | --- | --- | --- |
| Last Date Closed: |  |  |  |  |  |

Organization:

| JSA Type: |  |
| --- | --- |
| Work Type: |  |
| Work Activity: | Hot Work Activities |
| Specific Site: |  |

| Personal Protective Equipment (PPE) | Selected | Comments |
| --- | --- | --- |
| Hard Hat | Y | Required |
| Safety Glasses | Y | Required |
| Fire Resistant Clothing | Y |  |
| Face Shields | Y | As required |
| Hearing Protection |  |  |
| Goggles | Y | As required |
| Lifeline/Body Harness |  |  |
| Air Purifying Respirator |  |  |
| Supplied Air Respirator - SCBA |  |  |
| Welding Hood | Y |  |
| Welding/Pipe Clothing | Y | For welding jobs |
| Welding Mask/Goggles | Y |  |
| Personal Floatation Device |  |  |
| Long sleeve shirt | Y | Local procedure |
| Gloves | Y | Leather |
| Other |  |  |
| Safety Cones/Barricades | Y |  |
| Safety Vest | Y |  |
| Knee Pads |  |  |
| Caution Tape |  |  |
| Back Belt/Support |  |  |
| Substantial leather footwear |  |  |
| Winter Clothing |  |  |
| Safety Footwear | Y |  |
| Personal Gas Monitor |  |  |
| Long pants | Y |  |

Reviewers

| Reviewers Name | Position | Date Approved |
| --- | --- | --- |

Development Team

| Development Team Member Name | Primary Contact | Position |
| --- | --- | --- |

Job Steps

| No | Job Steps | Potential Hazard | Critical Actions |
| --- | --- | --- | --- |
| 1 | Complete General Work Permit | High risk work Non-routine and/or periodic work where approved work procedures do not exist | Complete permit and implement controls required |
| 2 | Conduct hazard assessment & write JSA(s) | High risk work Non-routine and/or periodic work where approved work procedures do not exist | Ensure qualified personnel conduct hazard assessment & write JSA(s) |
| 3 | Create a written work plan | High risk work Non-routine and/or periodic work where approved work procedures do not exist | Ensure plan describes in detail the activities, tasks and sub-tasks required to complete a specific scope of work |
| 4 | Conduct Job Site/Equipment Preparation (e.g., isolation, depressurization, purging, flushing, sealing all drains, etc…) (separate JSA(s) may be required to address specific job) | Flammable vapors (% LFL) Toxic gases/vapors Oxygen deficient/enriched As determined during Step 2 | Ensure equipment to be worked on is cleaned of all flammable/combustible materials Ensure combustible materials that cannot be removed are covered with flameproof material. Ensure oily surfaces and oil spills are rinsed and covered with at least 25 mm of sand. Ensure trash, oily rags, grass, weeds, etc are removed. Ensure pressure relief valves on pipelines and vessels adjacent to the work area are properly piped or vented to the safe area. |
| 5 | Initial Gas Testing | Flammable vapors (% LFL) Toxic gases/vapors Oxygen deficient/enriched As determined during Step 2 | Ensure gas testing performed in surrounding area for a distance of 15 meters (50 feet) Ensure LFL is 0% Ensure no residues of combustible liquids present. Ensure all potential areas are tested (e.g., adjacent to welded seams, plates, etc…) Determine follow-up gas testing requirements |
| 6 | Finalize & Issue Hot Work Permit | As determined during Step 2 | Ensure all identified requirements and controls have been implemented before signing permit |
| 7 | Conduct Safety Briefing | Inadequate communication to all personnel involved | Ensure the following topics are covered: Scope of work Conditions and requirements listed on permits and JSA(s). Potential hazards and controls Emergency response requirements Minimum PPE required |
| 8 | Begin Hot Work (e.g., welding, cutting, etc.) (separate JSA(s) may be required to address specific job tasks within this step) | Fire Flammable vapors (% LFL) Toxic gases/vapors Oxygen deficiency | Wear proper PPE, including welding helmet and respiratory protection if applicable. Ensure continuous gas testing occurs, if required Ensure fire extinguisher is readily available Ensure fire watch is available, if required Ensure welding/cutting equipment is in good working condition Ensure barriers are set-up contain any flying debris |
| 9 | Work Stoppages (permit cancellations, extensions, and revalidations) | May include but not limited to: Change in scope of work Change in entire work crew Change in site conditions Failure to conduct gas testing Issue with permits | Ensure Permit Issuer re-evaluates permit requirements and controls if any work stoppages occur |
| 10 | Work Completion | Job site not left in safe, clean, and/or orderly condition Adequate time has elapsed for the Fire Watch to verify condition of the job site Work performed does not meet required scope and specifications | Ensure Permit Issuer reviews job site prior to signing off on job Retain permits and supporting documentation in accordance with requirements |
| 11 | Assess any changing conditions, such as weather, traffic etc Update hazard and critical actions |  |  |